## Sheet1
A kolununda aşağıdaki değerler güç alanını ifade eder.(Power). Yandaki değerler ise Primary_Voltage alanında (Primer Gerilim) alanından alınmaktadır. | Pos. Seq. | 34,5 Kv | 15,8 Kv | 6,3 Kv | Zero Seq. | 34,5 Kv | 15,8 Kv | 6,3 Kv
10 Kva | R | 4.4 | 3.5 | 3.5 | Ro | 4.4 | 3.5 | 3.5
| X | 0.9434 | 1.9365 | 1.9365 | Xo | 0.09434 | 0.19365 | 0.19365
15 Kva | R | 4 | 3 | 3 | Ro | 4 | 3 | 3
| X | 2.0616 | 2.6458 | 2.6458 | Xo | 0.20616 | 0.26458 | 0.26458
25 Kva | R | 3.2 | 2.8 | 2.8 | Ro | 3.2 | 2.8 | 2.8
| X | 3.1639 | 2.8566 | 2.8566 | Xo | 0.31639 | 0.28566 | 0.28566
40 Kva | R | 4.28 | 3.76 | 3.76 | Ro | 4.28 | 3.76 | 3.76
| X | 1.3898 | 1.3647 | 1.3647 | Xo | 0.13898 | 0.13647 | 0.13647
50 Kva | R | 2.5 | 2.2 | 2.2 | Ro | 2.5 | 2.2 | 2.2
| X | 3.7417 | 3.3407 | 3.3407 | Xo | 0.37417 | 0.33407 | 0.33407
60 Kva | R | 2.25 | 2 | 2 | Ro | 2.25 | 2 | 2
| X | 3.8971 | 3.4641 | 3.4641 | Xo | 0.38971 | 0.34641 | 0.34641
63 Kva | R | 2.2698 | 2.0159 | 2.0159 | Ro | 2.2698 | 2.0159 | 2.0159
| X | 3.8856 | 3.4549 | 3.4549 | Xo | 0.38856 | 0.34549 | 0.34549
70 Kva | R | 2.1571 | 1.8929 | 1.8929 | Ro | 2.1571 | 1.8929 | 1.8929
| X | 3.9493 | 3.5238 | 3.5238 | Xo | 0.39493 | 0.35238 | 0.35238
73 Kva | R | 2.1781 | 1.8836 | 1.8836 | Ro | 2.1781 | 1.8836 | 1.8836
| X | 3.9378 | 3.5288 | 3.5288 | Xo | 0.39378 | 0.35288 | 0.35288
80 Kva | R | 2.0875 | 1.7875 | 1.7875 | Ro | 2.0875 | 1.7875 | 1.7875
| X | 3.9865 | 3.5784 | 3.5784 | Xo | 0.39865 | 0.35784 | 0.35784
100 Kva | R | 1.95 | 1.75 | 1.75 | Ro | 1.95 | 1.75 | 1.75
| X | 4.0556 | 3.5969 | 3.5969 | Xo | 0.40556 | 0.35969 | 0.35969
125 Kva | R | 1.76 | 1.6 | 1.6 | Ro | 1.76 | 1.6 | 1.6
| X | 4.1415 | 3.6661 | 3.6661 | Xo | 0.41415 | 0.36661 | 0.36661
150 Kva | R | 1.5938 | 1.4688 | 1.4688 | Ro | 1.5938 | 1.4688 | 1.4688
| X | 4.2083 | 3.7206 | 3.7206 | Xo | 0.42083 | 0.37206 | 0.37206
160 Kva | R | 1.5938 | 1.4688 | 1.4688 | Ro | 1.5938 | 1.4688 | 1.4688
| X | 4.2083 | 3.7206 | 3.7206 | Xo | 0.42083 | 0.37206 | 0.37206
180 Kva | R | 1.5278 | 1.4167 | 1.4167 | Ro | 1.5278 | 1.4167 | 1.4167
| X | 4.2327 | 3.7407 | 3.7407 | Xo | 0.42327 | 0.37407 | 0.37407
200 Kva | R | 1.475 | 1.375 | 1.375 | Ro | 1.475 | 1.375 | 1.375
| X | 4.2514 | 3.7562 | 3.7562 | Xo | 0.42514 | 0.37562 | 0.37562
250 Kva | R | 1.4 | 1.3 | 1.3 | Ro | 1.4 | 1.3 | 1.3
| X | 4.2767 | 3.7829 | 3.7829 | Xo | 2.9937 | 2.648 | 2.648
315 Kva | R | 1.3048 | 1.2175 | 1.2175 | Ro | 1.3048 | 1.2175 | 1.2175
| X | 4.3067 | 3.8102 | 3.8102 | Xo | 3.0147 | 2.6672 | 2.6672
400 Kva | R | 1.225 | 1.15 | 1.15 | Ro | 1.225 | 1.15 | 1.15
| X | 4.3301 | 3.8311 | 3.8311 | Xo | 3.031 | 2.6818 | 2.6818
500 Kva | R | 1.14 | 1.085 | 1.085 | Ro | 1.14 | 1.085 | 1.085
| X | 4.3532 | 3.85 | 3.85 | Xo | 3.0472 | 2.695 | 2.695
630 Kva | R | 1.0556 | 1.0317 | 1.0317 | Ro | 1.0556 | 1.0317 | 1.0317
| X | 4.3744 | 3.8646 | 3.8646 | Xo | 3.0621 | 2.7053 | 2.7053
750 Kva | R | 0.98 | 1 | 1 | Ro | 0.98 | 1 | 1
| X | 5.9194 | 5.9161 | 5.9161 | Xo | 4.1436 | 4.1413 | 4.1413
800 Kva | R | 1.0875 | 1.0625 | 1.0625 | Ro | 1.0875 | 1.0625 | 1.0625
| X | 5.9006 | 5.9052 | 5.9052 | Xo | 4.1304 | 4.1336 | 4.1336
850 Kva | R | 1.0941 | 1.0588 | 1.0588 | Ro | 1.0941 | 1.0588 | 1.0588
| X | 5.8994 | 5.9058 | 5.9058 | Xo | 4.1296 | 4.1341 | 4.1341
1000 Kva | R | 1.05 | 1.05 | 1.05 | Ro | 1.05 | 1.05 | 1.05
| X | 5.9074 | 5.9074 | 5.9074 | Xo | 4.1352 | 4.1352 | 4.1352
1200 Kva | R | 1.0417 | 1.0417 | 1.0417 | Ro | 1.0417 | 1.0417 | 1.0417
| X | 5.9089 | 5.9089 | 5.9089 | Xo | 4.1362 | 4.1362 | 4.1362
1250 Kva | R | 1.04 | 1.04 | 1.04 | Ro | 1.04 | 1.04 | 1.04
| X | 5.9092 | 5.9092 | 5.9092 | Xo | 4.1364 | 4.1364 | 4.1364
1500 Kva | R | 1.0333 | 1.0333 | 1.0333 | Ro | 1.0333 | 1.0333 | 1.0333
| X | 5.9103 | 5.9103 | 5.9103 | Xo | 4.1372 | 4.1372 | 4.1372
1600 Kva | R | 1.0625 | 1.0625 | 1.0625 | Ro | 1.0625 | 1.0625 | 1.0625
| X | 5.9052 | 5.9052 | 5.9052 | Xo | 4.1336 | 4.1336 | 4.1336
1650 Kva | R | 1.0909 | 1.0909 | 1.0909 | Ro | 1.0909 | 1.0909 | 1.0909
| X | 5.9 | 5.9 | 5.9 | Xo | 4.13 | 4.13 | 4.13
2000 Kva | R | 1.05 | 1.05 | 1.05 | Ro | 1.05 | 1.05 | 1.05
| X | 5.9074 | 5.9074 | 5.9074 | Xo | 4.1352 | 4.1352 | 4.1352
2180 Kva | R | 1.0092 | 1.0092 | 1.0092 | Ro | 1.0092 | 1.0092 | 1.0092
| X | 5.9145 | 5.9145 | 5.9145 | Xo | 4.1402 | 4.1402 | 4.1402
2200 Kva | R | 1.0227 | 1.0227 | 1.0227 | Ro | 1.0227 | 1.0227 | 1.0227
| X | 5.9122 | 5.9122 | 5.9122 | Xo | 4.1385 | 4.1385 | 4.1385
2500 Kva | R | 0.96 | 0.96 | 0.96 | Ro | 0.96 | 0.96 | 0.96
| X | 5.9227 | 5.9227 | 5.9227 | Xo | 4.1459 | 4.1459 | 4.1459
3150 Kva | R | 0.98413 | 0.98413 | 0.98413 | Ro | 0.98413 | 0.98413 | 0.98413
| X | 5.9187 | 5.9187 | 5.9187 | Xo | 4.1431 | 4.1431 | 4.1431
3200 Kva | R | 1 | 1 | 1 | Ro | 1 | 1 | 1
| X | 5.9161 | 5.9161 | 5.9161 | Xo | 4.1413 | 4.1413 | 4.1413
3300 Kva | R | 1.0152 | 1.0152 | 1.0152 | Ro | 1.0152 | 1.0152 | 1.0152
| X | 5.9135 | 5.9135 | 5.9135 | Xo | 4.1394 | 4.1394 | 4.1394
4000 Kva | R | 1.025 | 1.025 | 1.025 | Ro | 1.025 | 1.025 | 1.025
| X | 5.9118 | 5.9118 | 5.9118 | Xo | 4.1383 | 4.1383 | 4.1383
5000 Kva | R | 1.02 | 1.02 | 1.02 | Ro | 1.02 | 1.02 | 1.02
| X | 5.9127 | 5.9127 | 5.9127 | Xo | 4.1389 | 4.1389 | 4.1389
5750 Kva | R | 0.90435 | 0.90435 | 0.90435 | Ro | 0.90435 | 0.90435 | 0.90435
| X | 5.9315 | 5.9315 | 5.9315 | Xo | 4.152 | 4.152 | 4.152
6000 Kva | R | 1.0167 | 1.0167 | 1.0167 | Ro | 1.0167 | 1.0167 | 1.0167
| X | 5.9132 | 5.9132 | 5.9132 | Xo | 4.1393 | 4.1393 | 4.1393
6300 Kva | R | 0.97619 | 0.97619 | 0.97619 | Ro | 0.97619 | 0.97619 | 0.97619
| X | 5.9201 | 5.9201 | 5.9201 | Xo | 4.144 | 4.144 | 4.144
10 MVA | R | 1.02 | 1.02 | 1.02 | Ro | 1.02 | 1.02 | 1.02
| X | 7.6826 | 7.6826 | 7.6826 | Xo | 23.0478 | 23.0478 | 23.0478
16 MVA | R | 0.7875 | 0.7875 | 0.7875 | Ro | 0.7875 | 0.7875 | 0.7875
| X | 7.2373 | 7.2373 | 7.2373 | Xo | 21.7118 | 21.7118 | 21.7118
25 MVA | R | 0.54 | 0.54 | 0.54 | Ro | 0.54 | 0.54 | 0.54
| X | 11.9878 | 11.9878 | 11.9878 | Xo | 35.9635 | 35.9635 | 35.9635
30 MVA | R | 0.46667 | 0.46667 | 0.46667 | Ro | 0.46667 | 0.46667 | 0.46667
| X | 11.6907 | 11.6907 | 11.6907 | Xo | 35.0721 | 35.0721 | 35.0721
50 MVA | R | 0.54 | 0.54 | 0.54 | Ro | 0.54 | 0.54 | 0.54
| X | 12.0279 | 12.0279 | 12.0279 | Xo | 36.0836 | 36.0836 | 36.0836
80 MVA | R | 0.50625 | 0.50625 | 0.50625 | Ro | 0.50625 | 0.50625 | 0.50625
| X | 12.1895 | 12.1895 | 12.1895 | Xo | 36.5685 | 36.5685 | 36.5685
Note on B2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: R=Direnç (resistance) X = Reactance

## ImpedanceReference
Id | Sequence | Type | Primary_Voltage | Power | Result
1 | Positive | Resistance | 34.5 | 10 kVA | 4.4
2 | Positive | Resistance | 34.5 | 15 kVA | 4
3 | Positive | Resistance | 34.5 | 25 kVA | 3.2
4 | Positive | Resistance | 34.5 | 40 kVA | 4.28
5 | Positive | Resistance | 34.5 | 50 kVA | 2.5
6 | Positive | Resistance | 34.5 | 60 kVA | 2.25
7 | Positive | Resistance | 34.5 | 63 kVA | 2.2698
8 | Positive | Resistance | 34.5 | 70 kVA | 2.1571
9 | Positive | Resistance | 34.5 | 73 kVA | 2.1781
10 | Positive | Resistance | 34.5 | 80 kVA | 2.0875
11 | Positive | Resistance | 34.5 | 100 kVA | 1.95
12 | Positive | Resistance | 34.5 | 125 kVA | 1.76
13 | Positive | Resistance | 34.5 | 150 kVA | 1.5938
14 | Positive | Resistance | 34.5 | 160 kVA | 1.5938
15 | Positive | Resistance | 34.5 | 180 kVA | 1.5278
16 | Positive | Resistance | 34.5 | 200 kVA | 1.475
17 | Positive | Resistance | 34.5 | 250 kVA | 1.4
18 | Positive | Resistance | 34.5 | 315 kVA | 1.3048
19 | Positive | Resistance | 34.5 | 400 kVA | 1.225
20 | Positive | Resistance | 34.5 | 500 kVA | 1.14
21 | Positive | Resistance | 34.5 | 630 kVA | 1.0556
22 | Positive | Resistance | 34.5 | 750 kVA | 0.98
23 | Positive | Resistance | 34.5 | 800 kVA | 1.0875
24 | Positive | Resistance | 34.5 | 850 kVA | 1.0941
25 | Positive | Resistance | 34.5 | 1000 kVA | 1.05
26 | Positive | Resistance | 34.5 | 1200 kVA | 1.0417
27 | Positive | Resistance | 34.5 | 1250 kVA | 1.04
28 | Positive | Resistance | 34.5 | 1500 kVA | 1.0333
29 | Positive | Resistance | 34.5 | 1600 kVA | 1.0625
30 | Positive | Resistance | 34.5 | 1650 kVA | 1.0909
31 | Positive | Resistance | 34.5 | 2000 kVA | 1.05
32 | Positive | Resistance | 34.5 | 2180 kVA | 1.0092
33 | Positive | Resistance | 34.5 | 2200 kVA | 1.0227
34 | Positive | Resistance | 34.5 | 2500 kVA | 0.96
35 | Positive | Resistance | 34.5 | 3150 kVA | 0.98413
36 | Positive | Resistance | 34.5 | 3200 kVA | 1
37 | Positive | Resistance | 34.5 | 3300 kVA | 1.0152
38 | Positive | Resistance | 34.5 | 4000 kVA | 1.025
39 | Positive | Resistance | 34.5 | 5000 kVA | 1.02
40 | Positive | Resistance | 34.5 | 5750 kVA | 0.90435
41 | Positive | Resistance | 34.5 | 6000 kVA | 1.0167
42 | Positive | Resistance | 34.5 | 6300 kVA | 0.97619
43 | Positive | Resistance | 34.5 | 10 MVA | 1.02
44 | Positive | Resistance | 34.5 | 16 MVA | 0.7875
45 | Positive | Resistance | 34.5 | 25 MVA | 0.54
46 | Positive | Resistance | 34.5 | 30 MVA | 0.46667
47 | Positive | Resistance | 34.5 | 50 MVA | 0.54
48 | Positive | Resistance | 34.5 | 80 MVA | 0.50625
49 | Positive | Reactance | 34.5 | 10 kVA | 0.9434
50 | Positive | Reactance | 34.5 | 15 kVA | 2.0616
51 | Positive | Reactance | 34.5 | 25 kVA | 3.1639
52 | Positive | Reactance | 34.5 | 40 kVA | 1.3898
53 | Positive | Reactance | 34.5 | 50 kVA | 3.7417
54 | Positive | Reactance | 34.5 | 60 kVA | 3.8971
55 | Positive | Reactance | 34.5 | 63 kVA | 3.8856
56 | Positive | Reactance | 34.5 | 70 kVA | 3.9493
57 | Positive | Reactance | 34.5 | 73 kVA | 3.9378
58 | Positive | Reactance | 34.5 | 80 kVA | 3.9865
59 | Positive | Reactance | 34.5 | 100 kVA | 4.0556
60 | Positive | Reactance | 34.5 | 125 kVA | 4.1415
61 | Positive | Reactance | 34.5 | 150 kVA | 4.2083
62 | Positive | Reactance | 34.5 | 160 kVA | 4.2083
63 | Positive | Reactance | 34.5 | 180 kVA | 4.2327
64 | Positive | Reactance | 34.5 | 200 kVA | 4.2514
65 | Positive | Reactance | 34.5 | 250 kVA | 4.2767
66 | Positive | Reactance | 34.5 | 315 kVA | 4.3067
67 | Positive | Reactance | 34.5 | 400 kVA | 4.3301
68 | Positive | Reactance | 34.5 | 500 kVA | 4.3532
69 | Positive | Reactance | 34.5 | 630 kVA | 4.3744
70 | Positive | Reactance | 34.5 | 750 kVA | 5.9194
71 | Positive | Reactance | 34.5 | 800 kVA | 5.9006
72 | Positive | Reactance | 34.5 | 850 kVA | 5.8994
73 | Positive | Reactance | 34.5 | 1000 kVA | 5.9074
74 | Positive | Reactance | 34.5 | 1200 kVA | 5.9089
75 | Positive | Reactance | 34.5 | 1250 kVA | 5.9092
76 | Positive | Reactance | 34.5 | 1500 kVA | 5.9103
77 | Positive | Reactance | 34.5 | 1600 kVA | 5.9052
78 | Positive | Reactance | 34.5 | 1650 kVA | 5.9
79 | Positive | Reactance | 34.5 | 2000 kVA | 5.9074
80 | Positive | Reactance | 34.5 | 2180 kVA | 5.9145
81 | Positive | Reactance | 34.5 | 2200 kVA | 5.9122
82 | Positive | Reactance | 34.5 | 2500 kVA | 5.9227
83 | Positive | Reactance | 34.5 | 3150 kVA | 5.9187
84 | Positive | Reactance | 34.5 | 3200 kVA | 5.9161
85 | Positive | Reactance | 34.5 | 3300 kVA | 5.9135
86 | Positive | Reactance | 34.5 | 4000 kVA | 5.9118
87 | Positive | Reactance | 34.5 | 5000 kVA | 5.9127
88 | Positive | Reactance | 34.5 | 5750 kVA | 5.9315
89 | Positive | Reactance | 34.5 | 6000 kVA | 5.9132
90 | Positive | Reactance | 34.5 | 6300 kVA | 5.9201
91 | Positive | Reactance | 34.5 | 10 MVA | 7.6826
92 | Positive | Reactance | 34.5 | 16 MVA | 7.2373
93 | Positive | Reactance | 34.5 | 25 MVA | 11.9878
94 | Positive | Reactance | 34.5 | 30 MVA | 11.6907
95 | Positive | Reactance | 34.5 | 50 MVA | 12.0279
96 | Positive | Reactance | 34.5 | 80 MVA | 12.1895
97 | Positive | Resistance | 15.8 | 10 kVA | 3.5
98 | Positive | Resistance | 15.8 | 15 kVA | 3
99 | Positive | Resistance | 15.8 | 25 kVA | 2.8
100 | Positive | Resistance | 15.8 | 40 kVA | 3.76
101 | Positive | Resistance | 15.8 | 50 kVA | 2.2
102 | Positive | Resistance | 15.8 | 60 kVA | 2
103 | Positive | Resistance | 15.8 | 63 kVA | 2.0159
104 | Positive | Resistance | 15.8 | 70 kVA | 1.8929
105 | Positive | Resistance | 15.8 | 73 kVA | 1.8836
106 | Positive | Resistance | 15.8 | 80 kVA | 1.7875
107 | Positive | Resistance | 15.8 | 100 kVA | 1.75
108 | Positive | Resistance | 15.8 | 125 kVA | 1.6
109 | Positive | Resistance | 15.8 | 150 kVA | 1.4688
110 | Positive | Resistance | 15.8 | 160 kVA | 1.4688
111 | Positive | Resistance | 15.8 | 180 kVA | 1.4167
112 | Positive | Resistance | 15.8 | 200 kVA | 1.375
113 | Positive | Resistance | 15.8 | 250 kVA | 1.3
114 | Positive | Resistance | 15.8 | 315 kVA | 1.2175
115 | Positive | Resistance | 15.8 | 400 kVA | 1.15
116 | Positive | Resistance | 15.8 | 500 kVA | 1.085
117 | Positive | Resistance | 15.8 | 630 kVA | 1.0317
118 | Positive | Resistance | 15.8 | 750 kVA | 1
119 | Positive | Resistance | 15.8 | 800 kVA | 1.0625
120 | Positive | Resistance | 15.8 | 850 kVA | 1.0588
121 | Positive | Resistance | 15.8 | 1000 kVA | 1.05
122 | Positive | Resistance | 15.8 | 1200 kVA | 1.0417
123 | Positive | Resistance | 15.8 | 1250 kVA | 1.04
124 | Positive | Resistance | 15.8 | 1500 kVA | 1.0333
125 | Positive | Resistance | 15.8 | 1600 kVA | 1.0625
126 | Positive | Resistance | 15.8 | 1650 kVA | 1.0909
127 | Positive | Resistance | 15.8 | 2000 kVA | 1.05
128 | Positive | Resistance | 15.8 | 2180 kVA | 1.0092
129 | Positive | Resistance | 15.8 | 2200 kVA | 1.0227
130 | Positive | Resistance | 15.8 | 2500 kVA | 0.96
131 | Positive | Resistance | 15.8 | 3150 kVA | 0.98413
132 | Positive | Resistance | 15.8 | 3200 kVA | 1
133 | Positive | Resistance | 15.8 | 3300 kVA | 1.0152
134 | Positive | Resistance | 15.8 | 4000 kVA | 1.025
135 | Positive | Resistance | 15.8 | 5000 kVA | 1.02
136 | Positive | Resistance | 15.8 | 5750 kVA | 0.90435
137 | Positive | Resistance | 15.8 | 6000 kVA | 1.0167
138 | Positive | Resistance | 15.8 | 6300 kVA | 0.97619
139 | Positive | Resistance | 15.8 | 10 MVA | 1.02
140 | Positive | Resistance | 15.8 | 16 MVA | 0.7875
141 | Positive | Resistance | 15.8 | 25 MVA | 0.54
142 | Positive | Resistance | 15.8 | 30 MVA | 0.46667
143 | Positive | Resistance | 15.8 | 50 MVA | 0.54
144 | Positive | Resistance | 15.8 | 80 MVA | 0.50625
145 | Positive | Reactance | 15.8 | 10 kVA | 1.9365
146 | Positive | Reactance | 15.8 | 15 kVA | 2.6458
147 | Positive | Reactance | 15.8 | 25 kVA | 2.8566
148 | Positive | Reactance | 15.8 | 40 kVA | 1.3647
149 | Positive | Reactance | 15.8 | 50 kVA | 3.3407
150 | Positive | Reactance | 15.8 | 60 kVA | 3.4641
151 | Positive | Reactance | 15.8 | 63 kVA | 3.4549
152 | Positive | Reactance | 15.8 | 70 kVA | 3.5238
153 | Positive | Reactance | 15.8 | 73 kVA | 3.5288
154 | Positive | Reactance | 15.8 | 80 kVA | 3.5784
155 | Positive | Reactance | 15.8 | 100 kVA | 3.5969
156 | Positive | Reactance | 15.8 | 125 kVA | 3.6661
157 | Positive | Reactance | 15.8 | 150 kVA | 3.7206
158 | Positive | Reactance | 15.8 | 160 kVA | 3.7206
159 | Positive | Reactance | 15.8 | 180 kVA | 3.7407
160 | Positive | Reactance | 15.8 | 200 kVA | 3.7562
161 | Positive | Reactance | 15.8 | 250 kVA | 3.7829
162 | Positive | Reactance | 15.8 | 315 kVA | 3.8102
163 | Positive | Reactance | 15.8 | 400 kVA | 3.8311
164 | Positive | Reactance | 15.8 | 500 kVA | 3.85
165 | Positive | Reactance | 15.8 | 630 kVA | 3.8646
166 | Positive | Reactance | 15.8 | 750 kVA | 5.9161
167 | Positive | Reactance | 15.8 | 800 kVA | 5.9052
168 | Positive | Reactance | 15.8 | 850 kVA | 5.9058
169 | Positive | Reactance | 15.8 | 1000 kVA | 5.9074
170 | Positive | Reactance | 15.8 | 1200 kVA | 5.9089
171 | Positive | Reactance | 15.8 | 1250 kVA | 5.9092
172 | Positive | Reactance | 15.8 | 1500 kVA | 5.9103
173 | Positive | Reactance | 15.8 | 1600 kVA | 5.9052
174 | Positive | Reactance | 15.8 | 1650 kVA | 5.9
175 | Positive | Reactance | 15.8 | 2000 kVA | 5.9074
176 | Positive | Reactance | 15.8 | 2180 kVA | 5.9145
177 | Positive | Reactance | 15.8 | 2200 kVA | 5.9122
178 | Positive | Reactance | 15.8 | 2500 kVA | 5.9227
179 | Positive | Reactance | 15.8 | 3150 kVA | 5.9187
180 | Positive | Reactance | 15.8 | 3200 kVA | 5.9161
181 | Positive | Reactance | 15.8 | 3300 kVA | 5.9135
182 | Positive | Reactance | 15.8 | 4000 kVA | 5.9118
183 | Positive | Reactance | 15.8 | 5000 kVA | 5.9127
184 | Positive | Reactance | 15.8 | 5750 kVA | 5.9315
185 | Positive | Reactance | 15.8 | 6000 kVA | 5.9132
186 | Positive | Reactance | 15.8 | 6300 kVA | 5.9201
187 | Positive | Reactance | 15.8 | 10 MVA | 7.6826
188 | Positive | Reactance | 15.8 | 16 MVA | 7.2373
189 | Positive | Reactance | 15.8 | 25 MVA | 11.9878
190 | Positive | Reactance | 15.8 | 30 MVA | 11.6907
191 | Positive | Reactance | 15.8 | 50 MVA | 12.0279
192 | Positive | Reactance | 15.8 | 80 MVA | 12.1895
193 | Positive | Resistance | 6.3 | 10 kVA | 3.5
194 | Positive | Resistance | 6.3 | 15 kVA | 3
195 | Positive | Resistance | 6.3 | 25 kVA | 2.8
196 | Positive | Resistance | 6.3 | 40 kVA | 3.76
197 | Positive | Resistance | 6.3 | 50 kVA | 2.2
198 | Positive | Resistance | 6.3 | 60 kVA | 2
199 | Positive | Resistance | 6.3 | 63 kVA | 2.0159
200 | Positive | Resistance | 6.3 | 70 kVA | 1.8929
201 | Positive | Resistance | 6.3 | 73 kVA | 1.8836
202 | Positive | Resistance | 6.3 | 80 kVA | 1.7875
203 | Positive | Resistance | 6.3 | 100 kVA | 1.75
204 | Positive | Resistance | 6.3 | 125 kVA | 1.6
205 | Positive | Resistance | 6.3 | 150 kVA | 1.4688
206 | Positive | Resistance | 6.3 | 160 kVA | 1.4688
207 | Positive | Resistance | 6.3 | 180 kVA | 1.4167
208 | Positive | Resistance | 6.3 | 200 kVA | 1.375
209 | Positive | Resistance | 6.3 | 250 kVA | 1.3
210 | Positive | Resistance | 6.3 | 315 kVA | 1.2175
211 | Positive | Resistance | 6.3 | 400 kVA | 1.15
212 | Positive | Resistance | 6.3 | 500 kVA | 1.085
213 | Positive | Resistance | 6.3 | 630 kVA | 1.0317
214 | Positive | Resistance | 6.3 | 750 kVA | 1
215 | Positive | Resistance | 6.3 | 800 kVA | 1.0625
216 | Positive | Resistance | 6.3 | 850 kVA | 1.0588
217 | Positive | Resistance | 6.3 | 1000 kVA | 1.05
218 | Positive | Resistance | 6.3 | 1200 kVA | 1.0417
219 | Positive | Resistance | 6.3 | 1250 kVA | 1.04
220 | Positive | Resistance | 6.3 | 1500 kVA | 1.0333
221 | Positive | Resistance | 6.3 | 1600 kVA | 1.0625
222 | Positive | Resistance | 6.3 | 1650 kVA | 1.0909
223 | Positive | Resistance | 6.3 | 2000 kVA | 1.05
224 | Positive | Resistance | 6.3 | 2180 kVA | 1.0092
225 | Positive | Resistance | 6.3 | 2200 kVA | 1.0227
226 | Positive | Resistance | 6.3 | 2500 kVA | 0.96
227 | Positive | Resistance | 6.3 | 3150 kVA | 0.98413
228 | Positive | Resistance | 6.3 | 3200 kVA | 1
229 | Positive | Resistance | 6.3 | 3300 kVA | 1.0152
230 | Positive | Resistance | 6.3 | 4000 kVA | 1.025
231 | Positive | Resistance | 6.3 | 5000 kVA | 1.02
232 | Positive | Resistance | 6.3 | 5750 kVA | 0.90435
233 | Positive | Resistance | 6.3 | 6000 kVA | 1.0167
234 | Positive | Resistance | 6.3 | 6300 kVA | 0.97619
235 | Positive | Resistance | 6.3 | 10 MVA | 1.02
236 | Positive | Resistance | 6.3 | 16 MVA | 0.7875
237 | Positive | Resistance | 6.3 | 25 MVA | 0.54
238 | Positive | Resistance | 6.3 | 30 MVA | 0.46667
239 | Positive | Resistance | 6.3 | 50 MVA | 0.54
240 | Positive | Resistance | 6.3 | 80 MVA | 0.50625
241 | Positive | Reactance | 6.3 | 10 kVA | 1.9365
242 | Positive | Reactance | 6.3 | 15 kVA | 2.6458
243 | Positive | Reactance | 6.3 | 25 kVA | 2.8566
244 | Positive | Reactance | 6.3 | 40 kVA | 1.3647
245 | Positive | Reactance | 6.3 | 50 kVA | 3.3407
246 | Positive | Reactance | 6.3 | 60 kVA | 3.4641
247 | Positive | Reactance | 6.3 | 63 kVA | 3.4549
248 | Positive | Reactance | 6.3 | 70 kVA | 3.5238
249 | Positive | Reactance | 6.3 | 73 kVA | 3.5288
250 | Positive | Reactance | 6.3 | 80 kVA | 3.5784
251 | Positive | Reactance | 6.3 | 100 kVA | 3.5969
252 | Positive | Reactance | 6.3 | 125 kVA | 3.6661
253 | Positive | Reactance | 6.3 | 150 kVA | 3.7206
254 | Positive | Reactance | 6.3 | 160 kVA | 3.7206
255 | Positive | Reactance | 6.3 | 180 kVA | 3.7407
256 | Positive | Reactance | 6.3 | 200 kVA | 3.7562
257 | Positive | Reactance | 6.3 | 250 kVA | 3.7829
258 | Positive | Reactance | 6.3 | 315 kVA | 3.8102
259 | Positive | Reactance | 6.3 | 400 kVA | 3.8311
260 | Positive | Reactance | 6.3 | 500 kVA | 3.85
261 | Positive | Reactance | 6.3 | 630 kVA | 3.8646
262 | Positive | Reactance | 6.3 | 750 kVA | 5.9161
263 | Positive | Reactance | 6.3 | 800 kVA | 5.9052
264 | Positive | Reactance | 6.3 | 850 kVA | 5.9058
265 | Positive | Reactance | 6.3 | 1000 kVA | 5.9074
266 | Positive | Reactance | 6.3 | 1200 kVA | 5.9089
267 | Positive | Reactance | 6.3 | 1250 kVA | 5.9092
268 | Positive | Reactance | 6.3 | 1500 kVA | 5.9103
269 | Positive | Reactance | 6.3 | 1600 kVA | 5.9052
270 | Positive | Reactance | 6.3 | 1650 kVA | 5.9
271 | Positive | Reactance | 6.3 | 2000 kVA | 5.9074
272 | Positive | Reactance | 6.3 | 2180 kVA | 5.9145
273 | Positive | Reactance | 6.3 | 2200 kVA | 5.9122
274 | Positive | Reactance | 6.3 | 2500 kVA | 5.9227
275 | Positive | Reactance | 6.3 | 3150 kVA | 5.9187
276 | Positive | Reactance | 6.3 | 3200 kVA | 5.9161
277 | Positive | Reactance | 6.3 | 3300 kVA | 5.9135
278 | Positive | Reactance | 6.3 | 4000 kVA | 5.9118
279 | Positive | Reactance | 6.3 | 5000 kVA | 5.9127
280 | Positive | Reactance | 6.3 | 5750 kVA | 5.9315
281 | Positive | Reactance | 6.3 | 6000 kVA | 5.9132
282 | Positive | Reactance | 6.3 | 6300 kVA | 5.9201
283 | Positive | Reactance | 6.3 | 10 MVA | 7.6826
284 | Positive | Reactance | 6.3 | 16 MVA | 7.2373
285 | Positive | Reactance | 6.3 | 25 MVA | 11.9878
286 | Positive | Reactance | 6.3 | 30 MVA | 11.6907
287 | Positive | Reactance | 6.3 | 50 MVA | 12.0279
288 | Positive | Reactance | 6.3 | 80 MVA | 12.1895
289 | Zero | Resistance | 34.5 | 10 kVA | 4.4
290 | Zero | Resistance | 34.5 | 15 kVA | 4
291 | Zero | Resistance | 34.5 | 25 kVA | 3.2
292 | Zero | Resistance | 34.5 | 40 kVA | 4.28
293 | Zero | Resistance | 34.5 | 50 kVA | 2.5
294 | Zero | Resistance | 34.5 | 60 kVA | 2.25
295 | Zero | Resistance | 34.5 | 63 kVA | 2.2698
296 | Zero | Resistance | 34.5 | 70 kVA | 2.1571
297 | Zero | Resistance | 34.5 | 73 kVA | 2.1781
298 | Zero | Resistance | 34.5 | 80 kVA | 2.0875
299 | Zero | Resistance | 34.5 | 100 kVA | 1.95
300 | Zero | Resistance | 34.5 | 125 kVA | 1.76
301 | Zero | Resistance | 34.5 | 150 kVA | 1.5938
302 | Zero | Resistance | 34.5 | 160 kVA | 1.5938
303 | Zero | Resistance | 34.5 | 180 kVA | 1.5278
304 | Zero | Resistance | 34.5 | 200 kVA | 1.475
305 | Zero | Resistance | 34.5 | 250 kVA | 1.4
306 | Zero | Resistance | 34.5 | 315 kVA | 1.3048
307 | Zero | Resistance | 34.5 | 400 kVA | 1.225
308 | Zero | Resistance | 34.5 | 500 kVA | 1.14
309 | Zero | Resistance | 34.5 | 630 kVA | 1.0556
310 | Zero | Resistance | 34.5 | 750 kVA | 0.98
311 | Zero | Resistance | 34.5 | 800 kVA | 1.0875
312 | Zero | Resistance | 34.5 | 850 kVA | 1.0941
313 | Zero | Resistance | 34.5 | 1000 kVA | 1.05
314 | Zero | Resistance | 34.5 | 1200 kVA | 1.0417
315 | Zero | Resistance | 34.5 | 1250 kVA | 1.04
316 | Zero | Resistance | 34.5 | 1500 kVA | 1.0333
317 | Zero | Resistance | 34.5 | 1600 kVA | 1.0625
318 | Zero | Resistance | 34.5 | 1650 kVA | 1.0909
319 | Zero | Resistance | 34.5 | 2000 kVA | 1.05
320 | Zero | Resistance | 34.5 | 2180 kVA | 1.0092
321 | Zero | Resistance | 34.5 | 2200 kVA | 1.0227
322 | Zero | Resistance | 34.5 | 2500 kVA | 0.96
323 | Zero | Resistance | 34.5 | 3150 kVA | 0.98413
324 | Zero | Resistance | 34.5 | 3200 kVA | 1
325 | Zero | Resistance | 34.5 | 3300 kVA | 1.0152
326 | Zero | Resistance | 34.5 | 4000 kVA | 1.025
327 | Zero | Resistance | 34.5 | 5000 kVA | 1.02
328 | Zero | Resistance | 34.5 | 5750 kVA | 0.90435
329 | Zero | Resistance | 34.5 | 6000 kVA | 1.0167
330 | Zero | Resistance | 34.5 | 6300 kVA | 0.97619
331 | Zero | Resistance | 34.5 | 10 MVA | 1.02
332 | Zero | Resistance | 34.5 | 16 MVA | 0.7875
333 | Zero | Resistance | 34.5 | 25 MVA | 0.54
334 | Zero | Resistance | 34.5 | 30 MVA | 0.46667
335 | Zero | Resistance | 34.5 | 50 MVA | 0.54
336 | Zero | Resistance | 34.5 | 80 MVA | 0.50625
337 | Zero | Reactance | 34.5 | 10 kVA | 0.09434
338 | Zero | Reactance | 34.5 | 15 kVA | 0.20616
339 | Zero | Reactance | 34.5 | 25 kVA | 0.31639
340 | Zero | Reactance | 34.5 | 40 kVA | 0.13898
341 | Zero | Reactance | 34.5 | 50 kVA | 0.37417
342 | Zero | Reactance | 34.5 | 60 kVA | 0.38971
343 | Zero | Reactance | 34.5 | 63 kVA | 0.38856
344 | Zero | Reactance | 34.5 | 70 kVA | 0.39493
345 | Zero | Reactance | 34.5 | 73 kVA | 0.39378
346 | Zero | Reactance | 34.5 | 80 kVA | 0.39865
347 | Zero | Reactance | 34.5 | 100 kVA | 0.40556
348 | Zero | Reactance | 34.5 | 125 kVA | 0.41415
349 | Zero | Reactance | 34.5 | 150 kVA | 0.42083
350 | Zero | Reactance | 34.5 | 160 kVA | 0.42083
351 | Zero | Reactance | 34.5 | 180 kVA | 0.42327
352 | Zero | Reactance | 34.5 | 200 kVA | 0.42514
353 | Zero | Reactance | 34.5 | 250 kVA | 2.9937
354 | Zero | Reactance | 34.5 | 315 kVA | 3.0147
355 | Zero | Reactance | 34.5 | 400 kVA | 3.031
356 | Zero | Reactance | 34.5 | 500 kVA | 3.0472
357 | Zero | Reactance | 34.5 | 630 kVA | 3.0621
358 | Zero | Reactance | 34.5 | 750 kVA | 4.1436
359 | Zero | Reactance | 34.5 | 800 kVA | 4.1304
360 | Zero | Reactance | 34.5 | 850 kVA | 4.1296
361 | Zero | Reactance | 34.5 | 1000 kVA | 4.1352
362 | Zero | Reactance | 34.5 | 1200 kVA | 4.1362
363 | Zero | Reactance | 34.5 | 1250 kVA | 4.1364
364 | Zero | Reactance | 34.5 | 1500 kVA | 4.1372
365 | Zero | Reactance | 34.5 | 1600 kVA | 4.1336
366 | Zero | Reactance | 34.5 | 1650 kVA | 4.13
367 | Zero | Reactance | 34.5 | 2000 kVA | 4.1352
368 | Zero | Reactance | 34.5 | 2180 kVA | 4.1402
369 | Zero | Reactance | 34.5 | 2200 kVA | 4.1385
370 | Zero | Reactance | 34.5 | 2500 kVA | 4.1459
371 | Zero | Reactance | 34.5 | 3150 kVA | 4.1431
372 | Zero | Reactance | 34.5 | 3200 kVA | 4.1413
373 | Zero | Reactance | 34.5 | 3300 kVA | 4.1394
374 | Zero | Reactance | 34.5 | 4000 kVA | 4.1383
375 | Zero | Reactance | 34.5 | 5000 kVA | 4.1389
376 | Zero | Reactance | 34.5 | 5750 kVA | 4.152
377 | Zero | Reactance | 34.5 | 6000 kVA | 4.1393
378 | Zero | Reactance | 34.5 | 6300 kVA | 4.144
379 | Zero | Reactance | 34.5 | 10 MVA | 23.0478
380 | Zero | Reactance | 34.5 | 16 MVA | 21.7118
381 | Zero | Reactance | 34.5 | 25 MVA | 35.9635
382 | Zero | Reactance | 34.5 | 30 MVA | 35.0721
383 | Zero | Reactance | 34.5 | 50 MVA | 36.0836
384 | Zero | Reactance | 34.5 | 80 MVA | 36.5685
385 | Zero | Resistance | 15.8 | 10 kVA | 3.5
386 | Zero | Resistance | 15.8 | 15 kVA | 3
387 | Zero | Resistance | 15.8 | 25 kVA | 2.8
388 | Zero | Resistance | 15.8 | 40 kVA | 3.76
389 | Zero | Resistance | 15.8 | 50 kVA | 2.2
390 | Zero | Resistance | 15.8 | 60 kVA | 2
391 | Zero | Resistance | 15.8 | 63 kVA | 2.0159
392 | Zero | Resistance | 15.8 | 70 kVA | 1.8929
393 | Zero | Resistance | 15.8 | 73 kVA | 1.8836
394 | Zero | Resistance | 15.8 | 80 kVA | 1.7875
395 | Zero | Resistance | 15.8 | 100 kVA | 1.75
396 | Zero | Resistance | 15.8 | 125 kVA | 1.6
397 | Zero | Resistance | 15.8 | 150 kVA | 1.4688
398 | Zero | Resistance | 15.8 | 160 kVA | 1.4688
399 | Zero | Resistance | 15.8 | 180 kVA | 1.4167
400 | Zero | Resistance | 15.8 | 200 kVA | 1.375
401 | Zero | Resistance | 15.8 | 250 kVA | 1.3
402 | Zero | Resistance | 15.8 | 315 kVA | 1.2175
403 | Zero | Resistance | 15.8 | 400 kVA | 1.15
404 | Zero | Resistance | 15.8 | 500 kVA | 1.085
405 | Zero | Resistance | 15.8 | 630 kVA | 1.0317
406 | Zero | Resistance | 15.8 | 750 kVA | 1
407 | Zero | Resistance | 15.8 | 800 kVA | 1.0625
408 | Zero | Resistance | 15.8 | 850 kVA | 1.0588
409 | Zero | Resistance | 15.8 | 1000 kVA | 1.05
410 | Zero | Resistance | 15.8 | 1200 kVA | 1.0417
411 | Zero | Resistance | 15.8 | 1250 kVA | 1.04
412 | Zero | Resistance | 15.8 | 1500 kVA | 1.0333
413 | Zero | Resistance | 15.8 | 1600 kVA | 1.0625
414 | Zero | Resistance | 15.8 | 1650 kVA | 1.0909
415 | Zero | Resistance | 15.8 | 2000 kVA | 1.05
416 | Zero | Resistance | 15.8 | 2180 kVA | 1.0092
417 | Zero | Resistance | 15.8 | 2200 kVA | 1.0227
418 | Zero | Resistance | 15.8 | 2500 kVA | 0.96
419 | Zero | Resistance | 15.8 | 3150 kVA | 0.98413
420 | Zero | Resistance | 15.8 | 3200 kVA | 1
421 | Zero | Resistance | 15.8 | 3300 kVA | 1.0152
422 | Zero | Resistance | 15.8 | 4000 kVA | 1.025
423 | Zero | Resistance | 15.8 | 5000 kVA | 1.02
424 | Zero | Resistance | 15.8 | 5750 kVA | 0.90435
425 | Zero | Resistance | 15.8 | 6000 kVA | 1.0167
426 | Zero | Resistance | 15.8 | 6300 kVA | 0.97619
427 | Zero | Resistance | 15.8 | 10 MVA | 1.02
428 | Zero | Resistance | 15.8 | 16 MVA | 0.7875
429 | Zero | Resistance | 15.8 | 25 MVA | 0.54
430 | Zero | Resistance | 15.8 | 30 MVA | 0.46667
431 | Zero | Resistance | 15.8 | 50 MVA | 0.54
432 | Zero | Resistance | 15.8 | 80 MVA | 0.50625
433 | Zero | Reactance | 15.8 | 10 kVA | 0.19365
434 | Zero | Reactance | 15.8 | 15 kVA | 0.26458
435 | Zero | Reactance | 15.8 | 25 kVA | 0.28566
436 | Zero | Reactance | 15.8 | 40 kVA | 0.13647
437 | Zero | Reactance | 15.8 | 50 kVA | 0.33407
438 | Zero | Reactance | 15.8 | 60 kVA | 0.34641
439 | Zero | Reactance | 15.8 | 63 kVA | 0.34549
440 | Zero | Reactance | 15.8 | 70 kVA | 0.35238
441 | Zero | Reactance | 15.8 | 73 kVA | 0.35288
442 | Zero | Reactance | 15.8 | 80 kVA | 0.35784
443 | Zero | Reactance | 15.8 | 100 kVA | 0.35969
444 | Zero | Reactance | 15.8 | 125 kVA | 0.36661
445 | Zero | Reactance | 15.8 | 150 kVA | 0.37206
446 | Zero | Reactance | 15.8 | 160 kVA | 0.37206
447 | Zero | Reactance | 15.8 | 180 kVA | 0.37407
448 | Zero | Reactance | 15.8 | 200 kVA | 0.37562
449 | Zero | Reactance | 15.8 | 250 kVA | 2.648
450 | Zero | Reactance | 15.8 | 315 kVA | 2.6672
451 | Zero | Reactance | 15.8 | 400 kVA | 2.6818
452 | Zero | Reactance | 15.8 | 500 kVA | 2.695
453 | Zero | Reactance | 15.8 | 630 kVA | 2.7053
454 | Zero | Reactance | 15.8 | 750 kVA | 4.1413
455 | Zero | Reactance | 15.8 | 800 kVA | 4.1336
456 | Zero | Reactance | 15.8 | 850 kVA | 4.1341
457 | Zero | Reactance | 15.8 | 1000 kVA | 4.1352
458 | Zero | Reactance | 15.8 | 1200 kVA | 4.1362
459 | Zero | Reactance | 15.8 | 1250 kVA | 4.1364
460 | Zero | Reactance | 15.8 | 1500 kVA | 4.1372
461 | Zero | Reactance | 15.8 | 1600 kVA | 4.1336
462 | Zero | Reactance | 15.8 | 1650 kVA | 4.13
463 | Zero | Reactance | 15.8 | 2000 kVA | 4.1352
464 | Zero | Reactance | 15.8 | 2180 kVA | 4.1402
465 | Zero | Reactance | 15.8 | 2200 kVA | 4.1385
466 | Zero | Reactance | 15.8 | 2500 kVA | 4.1459
467 | Zero | Reactance | 15.8 | 3150 kVA | 4.1431
468 | Zero | Reactance | 15.8 | 3200 kVA | 4.1413
469 | Zero | Reactance | 15.8 | 3300 kVA | 4.1394
470 | Zero | Reactance | 15.8 | 4000 kVA | 4.1383
471 | Zero | Reactance | 15.8 | 5000 kVA | 4.1389
472 | Zero | Reactance | 15.8 | 5750 kVA | 4.152
473 | Zero | Reactance | 15.8 | 6000 kVA | 4.1393
474 | Zero | Reactance | 15.8 | 6300 kVA | 4.144
475 | Zero | Reactance | 15.8 | 10 MVA | 23.0478
476 | Zero | Reactance | 15.8 | 16 MVA | 21.7118
477 | Zero | Reactance | 15.8 | 25 MVA | 35.9635
478 | Zero | Reactance | 15.8 | 30 MVA | 35.0721
479 | Zero | Reactance | 15.8 | 50 MVA | 36.0836
480 | Zero | Reactance | 15.8 | 80 MVA | 36.5685
481 | Zero | Resistance | 6.3 | 10 kVA | 3.5
482 | Zero | Resistance | 6.3 | 15 kVA | 3
483 | Zero | Resistance | 6.3 | 25 kVA | 2.8
484 | Zero | Resistance | 6.3 | 40 kVA | 3.76
485 | Zero | Resistance | 6.3 | 50 kVA | 2.2
486 | Zero | Resistance | 6.3 | 60 kVA | 2
487 | Zero | Resistance | 6.3 | 63 kVA | 2.0159
488 | Zero | Resistance | 6.3 | 70 kVA | 1.8929
489 | Zero | Resistance | 6.3 | 73 kVA | 1.8836
490 | Zero | Resistance | 6.3 | 80 kVA | 1.7875
491 | Zero | Resistance | 6.3 | 100 kVA | 1.75
492 | Zero | Resistance | 6.3 | 125 kVA | 1.6
493 | Zero | Resistance | 6.3 | 150 kVA | 1.4688
494 | Zero | Resistance | 6.3 | 160 kVA | 1.4688
495 | Zero | Resistance | 6.3 | 180 kVA | 1.4167
496 | Zero | Resistance | 6.3 | 200 kVA | 1.375
497 | Zero | Resistance | 6.3 | 250 kVA | 1.3
498 | Zero | Resistance | 6.3 | 315 kVA | 1.2175
499 | Zero | Resistance | 6.3 | 400 kVA | 1.15
500 | Zero | Resistance | 6.3 | 500 kVA | 1.085
501 | Zero | Resistance | 6.3 | 630 kVA | 1.0317
502 | Zero | Resistance | 6.3 | 750 kVA | 1
503 | Zero | Resistance | 6.3 | 800 kVA | 1.0625
504 | Zero | Resistance | 6.3 | 850 kVA | 1.0588
505 | Zero | Resistance | 6.3 | 1000 kVA | 1.05
506 | Zero | Resistance | 6.3 | 1200 kVA | 1.0417
507 | Zero | Resistance | 6.3 | 1250 kVA | 1.04
508 | Zero | Resistance | 6.3 | 1500 kVA | 1.0333
509 | Zero | Resistance | 6.3 | 1600 kVA | 1.0625
510 | Zero | Resistance | 6.3 | 1650 kVA | 1.0909
511 | Zero | Resistance | 6.3 | 2000 kVA | 1.05
512 | Zero | Resistance | 6.3 | 2180 kVA | 1.0092
513 | Zero | Resistance | 6.3 | 2200 kVA | 1.0227
514 | Zero | Resistance | 6.3 | 2500 kVA | 0.96
515 | Zero | Resistance | 6.3 | 3150 kVA | 0.98413
516 | Zero | Resistance | 6.3 | 3200 kVA | 1
517 | Zero | Resistance | 6.3 | 3300 kVA | 1.0152
518 | Zero | Resistance | 6.3 | 4000 kVA | 1.025
519 | Zero | Resistance | 6.3 | 5000 kVA | 1.02
520 | Zero | Resistance | 6.3 | 5750 kVA | 0.90435
521 | Zero | Resistance | 6.3 | 6000 kVA | 1.0167
522 | Zero | Resistance | 6.3 | 6300 kVA | 0.97619
523 | Zero | Resistance | 6.3 | 10 MVA | 1.02
524 | Zero | Resistance | 6.3 | 16 MVA | 0.7875
525 | Zero | Resistance | 6.3 | 25 MVA | 0.54
526 | Zero | Resistance | 6.3 | 30 MVA | 0.46667
527 | Zero | Resistance | 6.3 | 50 MVA | 0.54
528 | Zero | Resistance | 6.3 | 80 MVA | 0.50625
529 | Zero | Reactance | 6.3 | 10 kVA | 0.19365
530 | Zero | Reactance | 6.3 | 15 kVA | 0.26458
531 | Zero | Reactance | 6.3 | 25 kVA | 0.28566
532 | Zero | Reactance | 6.3 | 40 kVA | 0.13647
533 | Zero | Reactance | 6.3 | 50 kVA | 0.33407
534 | Zero | Reactance | 6.3 | 60 kVA | 0.34641
535 | Zero | Reactance | 6.3 | 63 kVA | 0.34549
536 | Zero | Reactance | 6.3 | 70 kVA | 0.35238
537 | Zero | Reactance | 6.3 | 73 kVA | 0.35288
538 | Zero | Reactance | 6.3 | 80 kVA | 0.35784
539 | Zero | Reactance | 6.3 | 100 kVA | 0.35969
540 | Zero | Reactance | 6.3 | 125 kVA | 0.36661
541 | Zero | Reactance | 6.3 | 150 kVA | 0.37206
542 | Zero | Reactance | 6.3 | 160 kVA | 0.37206
543 | Zero | Reactance | 6.3 | 180 kVA | 0.37407
544 | Zero | Reactance | 6.3 | 200 kVA | 0.37562
545 | Zero | Reactance | 6.3 | 250 kVA | 2.648
546 | Zero | Reactance | 6.3 | 315 kVA | 2.6672
547 | Zero | Reactance | 6.3 | 400 kVA | 2.6818
548 | Zero | Reactance | 6.3 | 500 kVA | 2.695
549 | Zero | Reactance | 6.3 | 630 kVA | 2.7053
550 | Zero | Reactance | 6.3 | 750 kVA | 4.1413
551 | Zero | Reactance | 6.3 | 800 kVA | 4.1336
552 | Zero | Reactance | 6.3 | 850 kVA | 4.1341
553 | Zero | Reactance | 6.3 | 1000 kVA | 4.1352
554 | Zero | Reactance | 6.3 | 1200 kVA | 4.1362
555 | Zero | Reactance | 6.3 | 1250 kVA | 4.1364
556 | Zero | Reactance | 6.3 | 1500 kVA | 4.1372
557 | Zero | Reactance | 6.3 | 1600 kVA | 4.1336
558 | Zero | Reactance | 6.3 | 1650 kVA | 4.13
559 | Zero | Reactance | 6.3 | 2000 kVA | 4.1352
560 | Zero | Reactance | 6.3 | 2180 kVA | 4.1402
561 | Zero | Reactance | 6.3 | 2200 kVA | 4.1385
562 | Zero | Reactance | 6.3 | 2500 kVA | 4.1459
563 | Zero | Reactance | 6.3 | 3150 kVA | 4.1431
564 | Zero | Reactance | 6.3 | 3200 kVA | 4.1413
565 | Zero | Reactance | 6.3 | 3300 kVA | 4.1394
566 | Zero | Reactance | 6.3 | 4000 kVA | 4.1383
567 | Zero | Reactance | 6.3 | 5000 kVA | 4.1389
568 | Zero | Reactance | 6.3 | 5750 kVA | 4.152
569 | Zero | Reactance | 6.3 | 6000 kVA | 4.1393
570 | Zero | Reactance | 6.3 | 6300 kVA | 4.144
571 | Zero | Reactance | 6.3 | 10 MVA | 23.0478
572 | Zero | Reactance | 6.3 | 16 MVA | 21.7118
573 | Zero | Reactance | 6.3 | 25 MVA | 35.9635
574 | Zero | Reactance | 6.3 | 30 MVA | 35.0721
575 | Zero | Reactance | 6.3 | 50 MVA | 36.0836
576 | Zero | Reactance | 6.3 | 80 MVA | 36.5685